## Cable Schedule
ALDMOOR CONSULTING ENGINEERS
Northgate Water Treatment Works: Filter Block B
LV Power, Control and Instrumentation Cable Schedule
Doc No: ACE-2417-E-CS-001 Rev: B Date: 02/09/2026 Status: Issued for Construction
Cable No. | From | To | Cores | Size (mm²) | Cable Type | Voltage | Route Length (m) | Service / Remarks | Rev
POWER CABLES
FB-P-001A | LVSB-1 | MCC-B | 4 | 185 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 96 | MCC-B incomer, set 1 of 2
FB-P-001B | LVSB-1 | MCC-B | 4 | 185 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 96 | MCC-B incomer, set 2 of 2
FB-P-002 | MCC-B | BWP-1 | 4 | 95 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 78 | Backwash pump 1, 110 kW VSD
FB-P-003 | MCC-B | BWP-2 | 4 | 95 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 84 | Backwash pump 2, 110 kW VSD
FB-P-004 | MCC-B | ASB-1 | 4 | 35 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 64 | Air scour blower 1, 45 kW
FB-P-005 | MCC-B | ASB-2 | 4 | 35 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 71 | Air scour blower 2, 45 kW
FB-P-006 | MCC-B | WRP-1 | 4 | 16 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 112 | Washwater recovery pump 1, 15 kW
FB-P-007 | MCC-B | WRP-2 | 4 | 16 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 118 | Washwater recovery pump 2, 15 kW
FB-P-008 | MCC-B | DB-FB | 4 | 16 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 55 | Filter block distribution board
FB-P-010 | MCC-B | AV-11 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 22 | RGF-1 inlet valve actuator
FB-P-011 | MCC-B | AV-12 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 27 | RGF-1 outlet valve actuator
FB-P-012 | MCC-B | AV-13 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 32 | RGF-1 backwash valve actuator
FB-P-013 | MCC-B | AV-14 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 27 | RGF-1 air scour valve actuator
FB-P-014 | MCC-B | AV-15 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 30 | RGF-1 drain valve actuator
FB-P-015 | MCC-B | AV-21 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 32 | RGF-2 inlet valve actuator
FB-P-016 | MCC-B | AV-22 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 28 | RGF-2 outlet valve actuator
FB-P-017 | MCC-B | AV-23 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 38 | RGF-2 backwash valve actuator
FB-P-018 | MCC-B | AV-24 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 31 | RGF-2 air scour valve actuator
FB-P-019 | MCC-B | AV-25 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 36 | RGF-2 drain valve actuator
FB-P-020 | MCC-B | AV-31 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 33 | RGF-3 inlet valve actuator
FB-P-021 | MCC-B | AV-32 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 39 | RGF-3 outlet valve actuator
FB-P-022 | MCC-B | AV-33 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 39 | RGF-3 backwash valve actuator
FB-P-023 | MCC-B | AV-34 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 38 | RGF-3 air scour valve actuator
FB-P-024 | MCC-B | AV-35 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 45 | RGF-3 drain valve actuator
FB-P-025 | MCC-B | AV-41 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 33 | RGF-4 inlet valve actuator
FB-P-026 | MCC-B | AV-42 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 43 | RGF-4 outlet valve actuator
FB-P-027 | MCC-B | AV-43 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 37 | RGF-4 backwash valve actuator
FB-P-028 | MCC-B | AV-44 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 39 | RGF-4 air scour valve actuator
FB-P-029 | MCC-B | AV-45 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 50 | RGF-4 drain valve actuator
FB-P-030 | MCC-B | AV-51 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 45 | RGF-5 inlet valve actuator
FB-P-031 | MCC-B | AV-52 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 47 | RGF-5 outlet valve actuator
FB-P-032 | MCC-B | AV-53 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 44 | RGF-5 backwash valve actuator
FB-P-033 | MCC-B | AV-54 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 48 | RGF-5 air scour valve actuator
FB-P-034 | MCC-B | AV-55 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 52 | RGF-5 drain valve actuator
FB-P-035 | MCC-B | AV-61 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 41 | RGF-6 inlet valve actuator
FB-P-036 | MCC-B | AV-62 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 48 | RGF-6 outlet valve actuator
FB-P-037 | MCC-B | AV-63 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 50 | RGF-6 backwash valve actuator
FB-P-038 | MCC-B | AV-64 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 55 | RGF-6 air scour valve actuator
FB-P-039 | MCC-B | AV-65 | 4 | 2.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 50 | RGF-6 drain valve actuator
CONTROL CABLES
FB-C-001 | MCC-B | LCS-BWP1 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 74 | Backwash pump 1 local control station
FB-C-002 | MCC-B | LCS-BWP2 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 80 | Backwash pump 2 local control station
FB-C-003 | MCC-B | LCS-ASB1 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 61 | Air scour blower 1 local control station
FB-C-004 | MCC-B | LCS-ASB2 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 67 | Air scour blower 2 local control station
FB-C-005 | MCC-B | LCS-WRP1 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 108 | Washwater recovery pump 1 local control station
FB-C-006 | MCC-B | LCS-WRP2 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 114 | Washwater recovery pump 2 local control station
FB-C-007 | PLC-B | FCP-1 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 45 | RGF-1 filter control panel
FB-C-008 | PLC-B | FCP-2 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 56 | RGF-2 filter control panel
FB-C-009 | PLC-B | FCP-3 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 62 | RGF-3 filter control panel
FB-C-010 | PLC-B | FCP-4 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 66 | RGF-4 filter control panel
FB-C-011 | PLC-B | FCP-5 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 77 | RGF-5 filter control panel
FB-C-012 | PLC-B | FCP-6 | 12 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 87 | RGF-6 filter control panel
FB-C-020 | FCP-1 | AV-11 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 25 | RGF-1 inlet valve control
FB-C-021 | FCP-1 | AV-12 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 27 | RGF-1 outlet valve control
FB-C-022 | FCP-1 | AV-13 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 25 | RGF-1 backwash valve control
FB-C-023 | FCP-1 | AV-14 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 29 | RGF-1 air scour valve control
FB-C-024 | FCP-1 | AV-15 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 31 | RGF-1 drain valve control
FB-C-025 | FCP-2 | AV-21 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 23 | RGF-2 inlet valve control
FB-C-026 | FCP-2 | AV-22 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 23 | RGF-2 outlet valve control
FB-C-027 | FCP-2 | AV-23 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 24 | RGF-2 backwash valve control
FB-C-028 | FCP-2 | AV-24 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 34 | RGF-2 air scour valve control
FB-C-029 | FCP-2 | AV-25 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 28 | RGF-2 drain valve control
FB-C-030 | FCP-3 | AV-31 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 30 | RGF-3 inlet valve control
FB-C-031 | FCP-3 | AV-32 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 33 | RGF-3 outlet valve control
FB-C-032 | FCP-3 | AV-33 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 30 | RGF-3 backwash valve control
FB-C-033 | FCP-3 | AV-34 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 33 | RGF-3 air scour valve control
FB-C-034 | FCP-3 | AV-35 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 42 | RGF-3 drain valve control
FB-C-035 | FCP-4 | AV-41 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 32 | RGF-4 inlet valve control
FB-C-036 | FCP-4 | AV-42 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 38 | RGF-4 outlet valve control
FB-C-037 | FCP-4 | AV-43 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 39 | RGF-4 backwash valve control
FB-C-038 | FCP-4 | AV-44 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 35 | RGF-4 air scour valve control
FB-C-039 | FCP-4 | AV-45 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 40 | RGF-4 drain valve control
FB-C-040 | FCP-5 | AV-51 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 34 | RGF-5 inlet valve control
FB-C-041 | FCP-5 | AV-52 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 44 | RGF-5 outlet valve control
FB-C-042 | FCP-5 | AV-53 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 40 | RGF-5 backwash valve control
FB-C-043 | FCP-5 | AV-54 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 46 | RGF-5 air scour valve control
FB-C-044 | FCP-5 | AV-55 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 50 | RGF-5 drain valve control
FB-C-045 | FCP-6 | AV-61 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 38 | RGF-6 inlet valve control
FB-C-046 | FCP-6 | AV-62 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 39 | RGF-6 outlet valve control
FB-C-047 | FCP-6 | AV-63 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 49 | RGF-6 backwash valve control
FB-C-048 | FCP-6 | AV-64 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 42 | RGF-6 air scour valve control
FB-C-049 | FCP-6 | AV-65 | 7 | 1.5 | Cu/XLPE/SWA/LSZH | 0.6/1kV | 47 | RGF-6 drain valve control
INSTRUMENT CABLES
FB-I-001 | FCP-1 | LT-101 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 34 | RGF-1 level transmitter
FB-I-002 | FCP-1 | AT-101 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 37 | RGF-1 turbidity analyser
FB-I-003 | FCP-1 | FIT-101 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 38 | RGF-1 outlet flow meter
FB-I-004 | FCP-2 | LT-102 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 38 | RGF-2 level transmitter
FB-I-005 | FCP-2 | AT-102 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 47 | RGF-2 turbidity analyser
FB-I-006 | FCP-2 | FIT-102 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 44 | RGF-2 outlet flow meter
FB-I-007 | FCP-3 | LT-103 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 47 | RGF-3 level transmitter
FB-I-008 | FCP-3 | AT-103 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 51 | RGF-3 turbidity analyser
FB-I-009 | FCP-3 | FIT-103 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 46 | RGF-3 outlet flow meter
FB-I-010 | FCP-4 | LT-104 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 47 | RGF-4 level transmitter
FB-I-011 | FCP-4 | AT-104 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 58 | RGF-4 turbidity analyser
FB-I-012 | FCP-4 | FIT-104 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 53 | RGF-4 outlet flow meter
FB-I-013 | FCP-5 | LT-105 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 53 | RGF-5 level transmitter
FB-I-014 | FCP-5 | AT-105 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 61 | RGF-5 turbidity analyser
FB-I-015 | FCP-5 | FIT-105 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 63 | RGF-5 outlet flow meter
FB-I-016 | FCP-6 | LT-106 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 61 | RGF-6 level transmitter
FB-I-017 | FCP-6 | AT-106 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 70 | RGF-6 turbidity analyser
FB-I-018 | FCP-6 | FIT-106 | 2P | 1 | Cu/PVC/OS/SWA/LSZH | 300/500V | 67 | RGF-6 outlet flow meter
[6 empty] | TOTAL | 4815
Notes:
1. Route lengths include 2 m per end for termination and 5% spare. Contractor to verify on site before cutting.
2. All power and control cables BS 5467/BS 6724 LSZH, 0.6/1 kV. Instrument cables BS EN 50288-7, collectively screened, SWA.